## Συγκεντρωτικά
CapEx | Α/Α | Σενάριο | Εξοπλισμός | Δίκτυο ΜΤ | Civil Works | Υ/Σ | Augmentation | Σύνολο | €/MW |  | NOTE
| 1 | Ζωοδόχος [1 Οικίσκο - 1 Εxport] | 7639115 | 1832798.0322 | 4500000 | 1476891.3115 | 0 | 15448804.3437 | 584773.97 |  |  | User Input
| 2 | Ζωοδόχος [0 Οικίσκο - 2 Εxport] | 7639115 | 1686374.6633 | 4500000 | 1476891.3115 | 0 | 15302380.9748 | 579231.4974 |  |  | Results
| 3 | Λαψίστα | 20167715 | 1526039.2173 | 14000000 | 3823108.6885 | 0 | 39516862.9058 | 577839.8786 |  |  | Auto Generated Values
| 4 | TESLA BESS | 7774888.7604 | 56610.9 | 235878.75 | 0 | 641500.1478 | 8708878.5582 | 659303.5131
|  | Ζωοδόχος | Λαψίστα | Κόστος Τεμαχίου |  |  |  | Κόστος Εξοπλισμού Ζωοδόχος | Κόστος Εξοπλισμού Λαψίστα
Εξοπλισμός | Panels | 45549 | 117909 | 135 |  |  |  | 6149115 | 15917715
| Inverter | 84 | 257 | 10000 |  |  |  | 840000 | 2570000
| Step-Up TF (6.6 MVA) | 5 | 8 | 130000 |  |  |  | 650000 | 1040000
| Step-Up TF (9.9 MVA) | 0 | 4 | 160000 |  |  |  | 0 | 640000
[8 empty] | 7639115 | 20167715 | ΣΥΝΟΛΟ
|  | Ζωοδόχος | Λαψίστα | BESS
| Power [MW] | 26.4184 | 68.3872 | 13.2092
OpEx | Α/Α | Σενάριο | O&M | Insurance | Security | Land Lease | Contingencies | Σύνολο | €/MW
| 1 | Ζωοδόχος [1 Οικίσκο - 1 Εxport] | 142659.468 | 154488.0434 | 7925.526 | 17462.5756 | 10567.368 | 333102.9811 | 12608.7397
| 2 | Ζωοδόχος [0 Οικίσκο - 2 Εxport] | 142659.468 | 153023.8097 | 7925.526 | 17462.5756 | 10567.368 | 331638.7474 | 12553.315
| 3 | Λαψίστα | 369290.988 | 395168.6291 | 20516.166 | 45203.9524 | 10567.368 | 840747.1035 | 12293.9213
| 4 | TESLA BESS | 41555.3821 | 58349.4863 | 3962.763 | 0 | 6604.605 | 110472.2364 | 2401.5704
Note on F1: Manousos Veisakis: Με βάση την Unagi που υπολογίζονται BoP ~270k€ και περιλαμβάνει Εξοπλισμό (χωρίς πάνελ), Δίκτυο ΜΤ και ΕΠΜ.
Note on B5: Manousos Veisakis: Values from Budgetary Offers file
Note on D16: Manousos Veisakis: For PV 200k€/MWp based on Unagi

## Εσωτερικό δίκτυο
α/α | Name | Power [MW] | Voltage |  | Sattelite Distance [m] | Weighted Distance [m] | Cable Type | Cross-Section [mm2] | Circuits | Satellite Topography Increase Factor | Termination Spare Length [m] | Trench Length [km] | Cable Length [km] | Cable Procurement [€/km] | Trench Procurement (Civil Works) [€/km] | Total Procurement Cost | Οικίσκος | IPPM | Οπτικό | Testing | Cross-Section [mm2] | Total Cable Length [km]
1 | Ζωοδόχος [1 Οικίσκο - 1 Εxport] | 26.41 | 33kV | Υ/Σ 5 -> Υ/Σ 6 | 209 | 243.63 | AL/XLPE/ALPE/HDPE/SCPE | 185 | 1 | 7% | 10 | 0.24363 | 0.73089 | 7291 | 30000 | 12637.819 |  |  | 155.9232 | 50000 | 185 | 4.9362
|  |  |  | Υ/Σ 6 -> CB | 704 | 773.28 | AL/XLPE/ALPE/HDPE/SCPE | 185 | 1 |  |  | 0.77328 | 2.3198 | 7291 | 30000 | 40112.3534 |  |  | 494.8992 |  | 500 | 0.2205
[21 empty] | 1000 | 45.5425
|  |  |  | Υ/Σ 1 -> Υ/Σ 2 | 300 | 341 | AL/XLPE/ALPE/HDPE/SCPE | 185 | 1 |  |  | 0.341 | 1.023 | 7291 | 30000 | 17688.693 |  |  | 218.24
|  |  |  | Υ/Σ 2 -> Υ/Σ 3 | 250 | 287.5 | AL/XLPE/ALPE/HDPE/SCPE | 185 | 1 |  |  | 0.2875 | 0.8625 | 7291 | 30000 | 14913.4875 |  |  | 184
|  |  |  | Υ/Σ 3 -> CB | 50 | 73.5 | AL/XLPE/ALPE/HDPE/SCPE | 500 | 1 |  |  | 0.0735 | 0.2205 | 13374.5 | 30000 | 5154.0773 |  |  | 47.04 |  | Fiber Cable | 16.8997
|  |  |  | CB -> Υ/Σ | 14169 | 15180.83 | AL/XLPE/ALPE/HDPE/SCPE | 1000 | 1 |  |  | 15.1808 | 45.5425 | 22413.5 | 30000 | 1476191.4996 | 150000 | 65000 | 9715.7312
[16 empty] | 1566697.9298 | 150000 | 65000 | 1100.1024 | 50000
[15 empty] | Total | 1832798.0322
α/α | Name | Power [MW] | Voltage |  | Sattelite Distance [m] | Weighted Distance [m] | Cable Type | Cross-Section [mm2] | Circuits | Satellite Topography Increase Factor | Termination Spare Length [m] | Trench Length [km] | Cable Length [km] | Cable Procurement [€/km] | Trench Procurement (Civil Works) [€/km] | Total Procurement Cost | Οικίσκος | IPPM | Οπτικό | Testing | Cross-Section [mm2] | Total Cable Length [km]
2 | Ζωοδόχος [0 Οικίσκο - 2 Εxport] | 26.41 | 33kV | Υ/Σ 5 -> Υ/Σ 6 | 209 | 243.63 | AL/XLPE/ALPE/HDPE/SCPE | 150 | 1 | 7% | 10 | 0.24363 | 0.73089 | 6486 | 30000 | 12049.4525 |  |  | 155.9232 | 50000 | 150 | 49.1347
|  |  |  | Υ/Σ 6 -> Υ/Σ | 14473 | 15506.11 | AL/XLPE/ALPE/HDPE/SCPE | 150 | 1 |  |  | 15.5061 | 46.5183 | 6486 | 45000 | 999492.8384 |  | 65000 | 9923.9104 |  | 400 | 45.5425
|  |  |  | Υ/Σ 1 -> Υ/Σ 2 | 300 | 341 | AL/XLPE/ALPE/HDPE/SCPE | 150 | 1 |  |  | 0.341 | 1.023 | 6486 | 30000 | 16865.178 |  |  | 218.24
|  |  |  | Υ/Σ 2 -> Υ/Σ 3 | 250 | 287.5 | AL/XLPE/ALPE/HDPE/SCPE | 150 | 1 |  |  | 0.2875 | 0.8625 | 6486 | 30000 | 14219.175 |  |  | 184 |  | Fiber Cable | 31.5591
|  |  |  | Υ/Σ 3 -> Υ/Σ | 14169 | 15180.83 | AL/XLPE/ALPE/HDPE/SCPE | 400 | 1 |  |  | 15.1808 | 45.5425 | 11166.5 | 0 | 508550.2146 | 0 | 65000 | 9715.7312
[16 empty] | 1551176.8585 | 0 | 65000 | 20197.8048 | 50000
[15 empty] | Total | 1686374.6633
α/α | Name | Power [MW] | Voltage |  | Sattelite Distance [m] | Weighted Distance [m] | Cable Type | Cross-Section [mm2] | Circuits | Satellite Topography Increase Factor | Termination Spare Length [m] | Trench Length [km] | Cable Length [km] | Cable Procurement [€/km] | Trench Procurement (Civil Works) [€/km] | Total Procurement Cost | Οικίσκος | IPPM | Οπτικό | Testing | Cross-Section [mm2] | Total Cable Length [km]
3 | Λαψίστα | 68.39 | 33kV | Υ/Σ 1 -> Υ/Σ 2 | 849 | 928.43 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 | 7% | 10 | 0.92843 | 2.7853 | 9568 | 30000 | 54502.5547 |  |  | 594.1952 | 50000 | 95 | 4.3775
|  |  |  | Υ/Σ 2 -> Υ/Σ 3 | 784 | 858.88 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 |  |  | 0.85888 | 2.5766 | 9568 | 30000 | 50419.6915 |  |  | 549.6832 |  | 300 | 6.7541
|  |  |  | Υ/Σ 3 -> Υ/Σ 4 | 415 | 464.05 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 |  |  | 0.46405 | 1.3921 | 9568 | 30000 | 27241.5912 |  |  | 296.992 |  | 800 | 10.7236
|  |  |  | Υ/Σ 4 -> Υ/Σ | 3322 | 3574.54 | AL/XLPE/ALPE/HDPE/SCPE | 800 | 1 |  |  | 3.5745 | 10.7236 | 18837 | 30000 | 309237.0299 |  | 65000 | 2287.7056
[21 empty] | Fiber Cable | 7.2851
|  |  |  | Υ/Σ 7 -> Υ/Σ 6A | 1345 | 1459.15 | AL/XLPE/ALPE/HDPE/SCPE | 95 | 1 |  |  | 1.4592 | 4.3775 | 5347.5 | 30000 | 67182.9139 |  |  | 933.856
|  |  |  | Υ/Σ 6Α -> Υ/Σ 6 | 232 | 268.24 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 |  |  | 0.26824 | 0.80472 | 9568 | 30000 | 15746.761 |  |  | 171.6736
|  |  |  | Υ/Σ 6 -> Υ/Σ | 3409 | 3667.63 | AL/XLPE/ALPE/HDPE/SCPE | 800 | 1 |  |  | 3.6676 | 11.0029 | 18837 | 30000 | 317290.3389 |  | 65000 | 2347.2832
|  |  |  | Υ/Σ 8 -> Υ/Σ 5 | 1701 | 1840.07 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 |  |  | 1.8401 | 5.5202 | 9568 | 30000 | 108019.4693 |  |  | 1177.6448
|  |  |  | Υ/Σ 5Α -> Υ/Σ 5Β | 191 | 224.37 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 |  |  | 0.22437 | 0.67311 | 9568 | 30000 | 13171.4165 |  |  | 143.5968
|  |  |  | Υ/Σ 5Β -> Υ/Σ 5 | 230 | 266.1 | AL/XLPE/ALPE/HDPE/SCPE | 300 | 1 |  |  | 0.2661 | 0.7983 | 9568 | 30000 | 15621.1344 |  |  | 170.304
|  |  |  | Υ/Σ 5 -> Υ/Σ | 3200 | 3444 | AL/XLPE/ALPE/HDPE/SCPE | 800 | 1 |  |  | 3.444 | 10.332 | 18837 | 30000 | 297943.884 | 0 | 65000 | 2204.16
[16 empty] | 1276376.7853 | 0 | 195000 | 4662.432 | 50000
[15 empty] | Total | 1526039.2173
Note on Q1: Manousos Veisakis: 1 circuit : 35000 €/km 2 circuits: 40000 €/km 3 circuits: 45000 €/km HDD: 700000 €/km (Multiple) HDD: 850000 €/km (Single)
Note on Q15: Manousos Veisakis: 1 circuit : 35000 €/km 2 circuits: 40000 €/km 3 circuits: 45000 €/km HDD: 700000 €/km (Multiple) HDD: 850000 €/km (Single)
Note on Q27: Manousos Veisakis: 1 circuit : 35000 €/km 2 circuits: 40000 €/km 3 circuits: 45000 €/km HDD: 700000 €/km (Multiple) HDD: 850000 €/km (Single)

## Εσωτερικό Δίκτυο Αναλυτικά
|  | Διαδρομή | Μέγιστη Ονομαστική Ισχύς | Μήκος | Ρεύμα | Ρεύμα με συντελεστή ισχύος | Συντελεστής λόγω γειτνίασης των καλωδίων | Συντελεστής λόγω βάθους | Τύπος Καλωδίου | Αριθμός Κυκλωμάτων | Διατομή Αγωγού | Max cable allowble current | Rac_max | Xac_max | Zac_max | Πτώση τάσης καλωδίου | Απώλειες ισχύος |  | Ποσοστιαία Απώλεια κλάδου
α/α |  |  | [MW] | [m] | [A] | [A] |  |  |  |  | [mm2] | [A] | [Ω/m] | [Ω/m] | [Ω/m] | [%] | Τελικά MW | Απώλεια MW | [%]
1 | Ζωοδόχος [1 Οικίσκο - 1 Εxport] | Υ/Σ 5 -> Υ/Σ 6 | 4.1 | 243.63 | 79.7016 | 82.1665 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 185 | 263.11 | 0.000211 | 0.000122 | 0.000211 | 0.015794 | 4.099 | 0.0010412 | 0.025395 | PASS | cosφ | 0.97
|  | Υ/Σ 6 -> CB | 8.36 | 773.28 | 162.5134 | 167.5396 | 0.73 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 185 | 231.41 | 0.000211 | 0.000122 | 0.000211 | 0.10222 | 8.3463 | 0.01374 | 0.16435 | PASS | sinφ | 0.2431
[21 empty] | Volt | 29700
|  | Υ/Σ 1 -> Υ/Σ 2 | 6.01 | 341 | 116.8308 | 120.4441 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 185 | 263.11 | 0.000211 | 0.000122 | 0.000211 | 0.032405 | 6.0069 | 0.0031313 | 0.052102 | PASS
|  | Υ/Σ 2 -> Υ/Σ 3 | 12.02 | 287.5 | 233.6616 | 240.8883 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 185 | 263.11 | 0.000211 | 0.000122 | 0.000211 | 0.054642 | 12.0094 | 0.01056 | 0.087855 | PASS
|  | Υ/Σ 3 -> CB | 18.05 | 73.5 | 350.8812 | 361.7332 | 0.73 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 500 | 391.28 | 7.97e-05 | 0.000104 | 7.97e-05 | 0.009184 | 18.0477 | 0.0022996 | 0.01274 | PASS
|  | CB -> Υ/Σ | 26.41 | 15180.83 | 513.3946 | 529.2728 | 0.73 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 1000 | 552.61 | 4.22e-05 | 9.3e-05 | 4.22e-05 | 1.719 | 25.8716 | 0.53838 | 2.0385 | PASS
2 | Ζωοδόχος [0 Οικίσκο - 2 Εxport] | Υ/Σ 5 -> Υ/Σ 6 | 4.1 | 243.63 | 79.7016 | 82.1665 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 150 | 233.23 | 0.000265 | 0.000127 | 0.000265 | 0.019407 | 4.0987 | 0.0013076 | 0.031894 | PASS
|  | Υ/Σ 6 -> Υ/Σ | 8.36 | 15506.11 | 162.5134 | 167.5396 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 150 | 233.23 | 0.000265 | 0.000127 | 0.000265 | 2.5185 | 8.014 | 0.34602 | 4.139 | PASS
|  | Υ/Σ 1 -> Υ/Σ 2 | 6.01 | 341 | 116.8308 | 120.4441 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 150 | 233.23 | 0.000265 | 0.000127 | 0.000265 | 0.039816 | 6.0061 | 0.0039327 | 0.065436 | PASS
|  | Υ/Σ 2 -> Υ/Σ 3 | 12.02 | 287.5 | 233.6616 | 240.8883 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 150 | 233.23 | 0.000265 | 0.000127 | 0.000265 | 0.067139 | 12.0067 | 0.013263 | 0.11034 | FAIL
|  | Υ/Σ 3 -> Υ/Σ | 18.05 | 15180.83 | 350.8812 | 361.7332 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 400 | 383.46 | 0.000101 | 0.000109 | 0.000101 | 2.3014 | 17.4481 | 0.60189 | 3.3346 | PASS
3 | Λαψίστα | Υ/Σ 1 -> Υ/Σ 2 | 4.6 | 928.43 | 89.4213 | 92.1869 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.043976 | 4.5969 | 0.0030535 | 0.06638 | PASS
|  | Υ/Σ 2 -> Υ/Σ 3 | 12 | 858.88 | 233.2728 | 240.4875 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.10613 | 11.9808 | 0.019223 | 0.16019 | PASS
|  | Υ/Σ 3 -> Υ/Σ 4 | 17 | 464.05 | 330.4699 | 340.6906 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.081232 | 16.9792 | 0.020845 | 0.12262 | FAIL
|  | Υ/Σ 4 -> Υ/Σ | 23 | 3574.54 | 447.1063 | 460.9343 | 0.73 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 800 | 497.86 | 5.09e-05 | 9.5e-05 | 5.09e-05 | 0.40202 | 22.884 | 0.11597 | 0.50421 | PASS
|  | Υ/Σ 7 -> Υ/Σ 6A | 9 | 1459.15 | 174.9546 | 180.3656 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 95 | 183.43 | 0.000411 | 0.000136 | 0.000411 | 0.38257 | 8.9415 | 0.058529 | 0.65032 | PASS
|  | Υ/Σ 6Α -> Υ/Σ 6 | 15 | 268.24 | 291.591 | 300.6093 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.041431 | 14.9906 | 0.0093808 | 0.062539 | PASS
|  | Υ/Σ 6 -> Υ/Σ | 21 | 3667.63 | 408.2275 | 420.8531 | 0.73 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 800 | 497.86 | 5.09e-05 | 9.5e-05 | 5.09e-05 | 0.37662 | 20.9008 | 0.099194 | 0.47235 | PASS
|  | Υ/Σ 8 -> Υ/Σ 5 | 4.2 | 1840.07 | 81.6455 | 84.1706 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.079578 | 4.195 | 0.0050451 | 0.12012 | PASS
|  | Υ/Σ 5Α -> Υ/Σ 5Β | 10.93 | 224.37 | 212.4727 | 219.044 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.025252 | 10.9258 | 0.0041662 | 0.038117 | PASS
|  | Υ/Σ 5Β -> Υ/Σ 5 | 17.66 | 266.1 | 343.2999 | 353.9174 | 0.83 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 300 | 340.3 | 0.000129 | 0.000113 | 0.000129 | 0.048389 | 17.6471 | 0.012899 | 0.073041 | FAIL
|  | Υ/Σ 7 -> Υ/Σ 6A | 24.39 | 1459.15 | 474.127 | 488.7908 | 0.73 | 1 | AL/XLPE/ALPE/HDPE/SCPE | 1 | 800 | 497.86 | 5.09e-05 | 9.5e-05 | 5.09e-05 | 0.17403 | 24.3368 | 0.053233 | 0.21826 | PASS

## Σύνδεση
Υ/Σ ΛΑΨΙΣΤΑ
| Χωρίς ΑΔΜΗΕ | Με ΑΔΜΗΕ
ΑΔΜΗΕ | 600000 | 600000
Μ/Σ Ισχύος 110 MVA | 1400000 | 1400000
AIS 150kV | 600000 | 300000
Κτήριο Υ/Σ | 1500000 | 750000
Αντιστάθμιση | 0 | 0
Λοιπά | 500000 | 250000
Νέα Προδιαγραφή | 700000 | 350000
| 5300000 | 3650000

## Cable Costs
| Voltage |  | Aluminum Price [€/km] |  |  |  | Copper Price [€/km]
Increase Factor | 20kV | Cross-Section [mm2] | AL/XLPE/CWS/HDPE | AL/XLPE/CWS/HDPE/SCPE | AL/XLPE/ALPE/HDPE | AL/XLPE/ALPE/HDPE/SCPE | CU/XLPE/CWS/HDPE | CU/XLPE/CWS/HDPE/SCPE | CU/XLPE/ALPE/HDPE | CU/XLPE/ALPE/HDPE/SCPE
15% |  | 95 | 5968.5 | 6589.5 | 3680 | 4289.5 | 0 | 0 | 0 | 0
|  | 120 | 6520.5 | 7176 | 4197.5 | 4830 | 0 | 0 | 0 | 0
|  | 150 | 7026.5 | 7705 | 4715 | 5393.5 | 0 | 0 | 0 | 0
|  | 185 | 7728 | 8452.5 | 5405 | 6095 | 0 | 0 | 0 | 0
|  | 240 | 8740 | 9510.5 | 6417 | 7164.5 | 0 | 0 | 0 | 0
|  | 300 | 9821 | 10626 | 7486.5 | 8291.5 | 0 | 0 | 0 | 0
|  | 400 | 11281.5 | 12155.5 | 8924 | 9775 | 0 | 0 | 0 | 0
|  | 500 | 13351.5 | 14294.5 | 10982.5 | 11914 | 66366.5 | 67206 | 64239 | 65090
|  | 630 | 15651.5 | 16663.5 | 13271 | 14271.5 | 83961.5 | 84881.5 | 81822.5 | 82731
|  | 800 | 18469 | 19584.5 | 16065.5 | 17158 | 106835 | 107812.5 | 104661.5 | 105639
|  | 1000 | 21896 | 23103.5 | 19423.5 | 20596.5 | 132894 | 133975 | 130663 | 131721
|  | 1200 | 26841 | 28175 | 24322.5 | 25645 | 156078 | 155974.5 | 152547.5 | 153720.5
|  |  | Aluminum Price [€/km] |  |  |  | Copper Price [€/km]
| 33kV | Cross-Section [mm2] | AL/XLPE/CWS/HDPE | AL/XLPE/CWS/HDPE/SCPE | AL/XLPE/ALPE/HDPE | AL/XLPE/ALPE/HDPE/SCPE | CU/XLPE/CWS/HDPE | CU/XLPE/CWS/HDPE/SCPE | CU/XLPE/ALPE/HDPE | CU/XLPE/ALPE/HDPE/SCPE
|  | 95 | 6957.5 | 7682 | 4646 | 5347.5 | 0 | 0 | 0 | 0
|  | 120 | 7337 | 8268.5 | 5186.5 | 5934 | 0 | 0 | 0 | 0
|  | 150 | 7889 | 8866.5 | 5715.5 | 6486 | 0 | 0 | 0 | 0
|  | 185 | 8625 | 9637 | 6474.5 | 7291 | 0 | 0 | 0 | 0
|  | 240 | 9717.5 | 10787 | 7555.5 | 8418 | 0 | 0 | 0 | 0
|  | 300 | 10844.5 | 11983 | 8671 | 9568 | 0 | 0 | 0 | 0
|  | 400 | 12374 | 13570 | 10200.5 | 11166.5 | 0 | 0 | 0 | 0
|  | 500 | 14513 | 15824 | 12316.5 | 13374.5 | 67631.5 | 68574.5 | 65435 | 66378
|  | 630 | 16893.5 | 18285 | 14743 | 15847 | 85307 | 86342 | 83145 | 84145.5
|  | 800 | 19814.5 | 21298 | 17652.5 | 18837 | 108272.5 | 109376.5 | 106087.5 | 107157
|  | 1000 | 23345 | 24943.5 | 21125.5 | 22413.5 | 134446.5 | 135619.5 | 132192.5 | 133354
|  | 1200 | 28922.5 | 30348.5 | 26151 | 27565.5 | 156618.5 | 157906.5 | 154169 | 156584
Increase Factor |  | Fiber Optic Cables | Cablel [€/km] | Nexans (Directly buried) [€/km] | Nexans (for ducts) [€/km]
60% |  | 6fb x 9/125 | 584 | 555.2 | 350.4
|  | 8fb x 9/125 | 600 | 571.2 | 371.2
|  | 12fb x 9/125 | 616 | 606.4 | 409.6
|  | 24fb x 9/125 | 640 | 808 | 560
|  | Grounding Rods/Conductors (Tinned Copper) |  |  | UG HVAC 150kV
|  | Cross-Section [mm2] | Cost [€/m] |  | Cross-Section [mm2] | Cost per phase [€/km] |  | Civil Works | Single-Circuit Cost [€/km] | Double-Circuit Cost [€/km]
|  | 50 | 5.3118 |  | 800 | 70000 |  | Ductbank | 400000 | 650000
|  | 70 | 7.4366 |  | 1000 | 75000 |  | Directly Buried | 300000 | 550000
|  | 95 | 10.0925 |  | 1200 | 80000
|  | 120 | 12.7484 |  | 1400 | 90000 |  |  | Cost [€/pit]
|  | 150 | 15.9355 |  | 1600 | 95000 |  | Jointing Works & Accessories | 45300
|  | 185 | 19.6538 |  | 1800 | 100000
OHL
|  | Type | Cost [€/m]
|  | Single-Circuit 150kV | 300
|  | Double-Circuit 150kV | 400
|  | Single-Circuit 400kV | 650
|  | Double-Circuit 400kV | 950
|  | TZ4 (150kV) | 500
|  | TZ4 (400kV) | 1000
Submarine Cable [Copper]
|  | Cross-Section [mm2] | Cost [€/m]
|  | 630 | 1700
|  | 800 | 1800
|  | 1000 | 1900
|  | 1200 | 2000
|  | 1400 | 2100
|  | 1600 | 2200
Note on J43: Manousos Veisakis: 1. Jointing Work: 5000 €/phase 2. Jointing Equipment: 3000 €/phase 3. Link Box : 1300 €/pit 4. Civil Works: 20000 €/pit
Note on C54: Manousos Veisakis: Not available in Greece.

## Cable Data
AL | Cross-Section [mm2] | Ampacity | Rdc(Ω/m) @20 oC | Rdc(Ω/m) @90 oC | R (Ω/m) @90 oC | X (Ω/m) @90 oC | Z (Ω/m) @90 oC | C (μF/m) | Ro (Ω/m) @90 oC | Xo (Ω/m) @90 oC
| 70 | 186 | 0.000443 | 0.00056799 | 0.000568 | 0.000143 | 0.00058572 | 0.00016 | 0.000384 | 8.3e-05
| 95 | 221 | 0.00032 | 0.00041027 | 0.000411 | 0.000136 | 0.00043292 | 0.00018 | 0.000305 | 7.7e-05
| 120 | 252 | 0.000253 | 0.00032437 | 0.0003247 | 0.00013 | 0.00034976 | 0.00019 | 0.000255 | 7.3e-05
| 150 | 281 | 0.000206 | 0.0002641 | 0.000265 | 0.000127 | 0.00029386 | 0.0002 | 0.000217 | 6.9e-05
| 185 | 317 | 0.000164 | 0.00021026 | 0.000211 | 0.000122 | 0.00024373 | 0.00022 | 0.000179 | 6.5e-05
| 240 | 367 | 0.000125 | 0.00016026 | 0.000161 | 0.000117 | 0.00019902 | 0.00024 | 0.000142 | 6e-05
| 300 | 410 | 0.0001 | 0.00012821 | 0.000129 | 0.000113 | 0.00017149 | 0.00026 | 0.000116 | 5.7e-05
| 400 | 462 | 7.78e-05 | 9.975e-05 | 0.000101 | 0.000109 | 0.0001486 | 0.00029 | 9.3e-05 | 5.2e-05
| 500 | 536 | 6.05e-05 | 7.757e-05 | 7.97e-05 | 0.000104 | 0.00013103 | 0.00032 | 7.5e-05 | 4.9e-05
| 630 | 600 | 4.69e-05 | 6.013e-05 | 6.3e-05 | 0.0001 | 0.00011819 | 0.00035 | 6e-05 | 4.7e-05
| 800 | 682 | 3.67e-05 | 4.705e-05 | 5.09e-05 | 9.5e-05 | 0.00010778 | 0.0004 | 4.9e-05 | 4.4e-05
| 1000 | 757 | 2.91e-05 | 3.731e-05 | 4.22e-05 | 9.3e-05 | 0.00010213 | 0.00044 | 4.1e-05 | 4e-05
| 1200 | 800 | 2.91e-05 | 3.731e-05 | 4.22e-05 | 9.3e-05 | 0.00010213 | 0.00044 | 4.1e-05 | 4e-05
CU | Cross-Section [mm2] | Ampacity | Rdc(Ω/m) @20 oC | Rdc(Ω/m) @90 oC | R (Ω/m) @90 oC | X (Ω/m) @90 oC | Z (Ω/m) @90 oC | C (μF/m) | Ro (Ω/m) @90 oC | Xo (Ω/m) @90 oC
95
120
150
185
240
300
400
500
| 630 | 753 | 2.83e-05 | 3.609e-05 | 4.05e-05 | 0.0001 | 0.00010789 | 0.00035 | 0.039 | 0.046
800
1000
1200
Depth of Laying [m] | Correction Factor |  | Derating Factors accornding to IEC 60502-2 for groups of three phase circuits of single core cables laid directly in the ground | [6 empty] | Grounding Rods/Conductors (Tinned Copper)
0.5 | 1.05 |  | Number of cables in Group | Spacing Between Group Centers [mm] | [5 empty] | Cross-Section [mm2] | Weight [kg/km]
0.6 | 1.03 |  |  | Touching | 200 | 400 | 600 | 800 |  | 50 | 429.3
0.8 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 |  | 70 | 607.1
1 | 0.97 |  | 2 | 0.73 | 0.83 | 0.88 | 0.9 | 0.92 |  | 95 | 841.4
1.25 | 0.95 |  | 3 | 0.6 | 0.73 | 0.79 | 0.83 | 0.86 |  | 120 | 1056.5
1.5 | 0.93 |  | 4 | 0.54 | 0.68 | 0.75 | 0.8 | 0.84 |  | 150 | 1300
1.75 | 0.92 |  | 5 | 0.49 | 0.63 | 0.72 | 0.78 | 0.82 |  | 185 | 1636.2
2 | 0.91 |  | 6 | 0.46 | 0.61 | 0.7 | 0.76 | 0.81 |  | 240 | 2155
2.5 | 0.89 |  | 7 | 0.43 | 0.58 | 0.68 | 0.75 | 0.8
3 | 0.88 |  | 8 | 0.41 | 0.57 | 0.67 | 0.74 | -
3.5 | 0.8198 |  | 9 | 0.39 | 0.55 | 0.66 | 0.73 | -
4 | 0.7866 |  | 10 | 0.37 | 0.54 | 0.65 | - | -
4.5 | 0.7535 |  | 11 | 0.36 | 0.53 | 0.64 | - | -
5 | 0.7204 |  | 12 | 0.35 | 0.52 | 0.64 | - | -